## Gate
STANDARD |  | AUSTRALIA | [8 empty] | EUROPEAN UNION | [12 empty] | INTERNATIONAL | [5 empty] | GERMANY | [6 empty] | USA | [5 empty] | UK | [19 empty] | JAPAN | [18 empty] | CHINA
|  | AS 1628:1999 WATER SUPPLY - METALIC GATE, GLOBE AND NON-RETURN VALVES |  |  | AS/NZS 2638.1:2011 GATE VALVES FOR WATERWORKS PURPOSES PART 1: METAL SEATED |  |  | AS/NZS 2638.2:2011 GATE VALVES FOR WATERWORKS PURPOSES PART 2. RESILIENT SEATED |  | AS 6401:2022 KNIFE-GATE VALVES FOR WATERWORKS PURPOSES | EN 558:2017 INDUSTRIAL VALVES - FACE-TO-FACE AND CENTRE-TO-FACE DIMENSIONS OF METAL VALVES FOR USE IN FLANGED PIPE SYSTEMS - PN AND CLASS DESIGNATED VALVES | [12 empty] | ISO 5752:2021 METAL VALVES FOR USE IN FLANGED PIPE SYSTEMS - FACE-TO-FACE AND CENTRE-TO-FACE DIMENSIONS | [5 empty] | DIN EN 558:2022 (FORMERLY DIN 3202 PART 1) INDUSTRIAL VALVE - FACE-TO-FACE AND CENTRE-TO-FACE DIMENSIONS OF METAL VALVE FOR USE IN FLANGED PIPE SYSTEMS - PN AND CLASS DESIGNATED VALVES | [6 empty] | ASME B16.10:2017 FACE-TO-FACE AND END-TO-END DIMENSIONS OF VALVES |  |  |  |  | MSS SP-81 STAINLESS-STEEL OR STAINLESS-STEEL-LINED, BONNETLESS, KNIFE GATE VALVE WITH FLANGED ENDS | BS EN 558:2022 (FORMERLY BS 2080) INDUSTRIAL VALVE - FACE-TO-FACE AND CENTRE-TO-FACE DIMENSIONS OF METAL VALVE FOR USE IN FLANGED PIPE SYSTEMS - PN AND CLASS DESIGNATED VALVES | [19 empty] | JIS B 2002 - 1987 FACE-TO-FACE AND END-TO-END DIMENSIONS OF VALVES | [18 empty] | GB/T 12221:2005 METAL VALVES - FACE TO FACE, END TO END, CENTER TO FACE AND CENTER TO END DIMENSIONS
AS 1628:1999 |  | AS 1628 | AS 1628 | AS 1628 | [8 empty] | AS 1628 LONG3 SERIES 7 |  |  | AS 1628 LONG4 SERIES 18 | [30 empty] | AS 1628 LONG4 SERIES 18 | AS 1628 LONG6 SERIES 7 | [8 empty] | AS 1628 LONG4 SERIES 18 | AS 1628 LONG6 SERIES 7 | [6 empty] | AS 1628 LONG4 SERIES 18 |  |  |  |  | AS 1628 LONG6 SERIES 7
AS/NZS 2638.1:2011 |  |  |  |  | AS/NZS 2638.1 | AS/NZS 2638.1 | AS/NZS 2638.1 | AS/NZS 2638.1 PN16 |  |  | AS/NZS 2638.1 PN16 | [12 empty] | AS/NZS 2638.1 PN16 | [12 empty] | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 |  |  |  |  | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 |  |  | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN16 | [16 empty] | AS/NZS 2638.1 PN16 | [13 empty] | AS/NZS 2638.1 PN16
AS/NZS 2638.2:2011 |  |  |  |  | AS/NZS 2638.2 PN16, PN25 |  |  | ASNZS 2638.2 | ASNZS 2638.2 |  | AS/NZS 2638.2 PN16, PN25 | [12 empty] | AS/NZS 2638.2 PN16, PN25 | [12 empty] | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 |  |  |  |  | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 |  |  | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 | AS/NZS 2638.2 PN16, PN25 | [16 empty] | AS/NZS 2638.2 PN16, PN25 | [13 empty] | AS/NZS 2638.2 PN16, PN25
AS 6401:2022 | [9 empty] | AS 6401 | [31 empty] | AS 6401
EN 558:2017 |  |  | EN 558 SERIES 7 | EN 558 SERIES 18 | EN 558 SERIES 3 |  | EN 558 SERIES 192 | EN 558 SERIES 3 | EN 558 SERIES 192 |  | EN 558 | EN 558 EN 528:2022 CLASS 300 ONLY | EN 558 | EN 558 | EN 558 | EN 558 | EN 558:2017 EN 528:2022 CLASS 250 ONLY, DN≥50 | EN 558 | EN 558 | EN 558 | EN 558 | EN 558 | EN 558 | EN 558 SERIES 3 | EN 558 SERIES 14 | EN 558 SERIES 15 | EN 558 SERIES 26 | EN 558 SERIES 19 | EN 558 SERIES 4 | EN 558:2022 SERIES 3 | EN 558 EN 528:2022 CLASS 300 ONLY | EN 558:2017 EN 528:2022 CLASS 250 ONLY, DN≥50 | EN 558:2022 SERIES 14 | EN 558:2022 SERIES 15 | EN 558 SERIES 26 | EN 558:2017 SERIES 47 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 19 | EN 558 SERIES 4 |  | EN 558 SERIES 14 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 18 | EN 558 SERIES 7 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 3 | EN 558 SERIES 4 | EN 558 | EN 558 | EN 558 SERIES 19 | EN 558 SERIES 19 | EN 558 SERIES 18 | EN 558 SERIES 7 | EN 558 SERIES 19 | EN 558 SERIES 4 | EN 558 SERIES 19 | EN 558 SERIES 4 | EN 558 SERIES 14 |  | EN 558 SERIES 18 |  |  | EN 558 SERIES 3 | EN 558 SERIES 15 | EN 558 SERIES 7 |  | EN 558 SERIES 4 | EN 558 SERIES 19 | [7 empty] | EN 558 SERIES 15 | EN 558 SERIES 3 | EN 558 SERIES 15 |  | EN 558 SERIES 15
ISO 5752:2021 |  |  | ISO 5752 SERIES 7 | ISO 5752 SERIES 18 | ISO 5752 SERIES 3 |  | ISO 5752 SERIES 192 | ISO 5752 SERIES 3 | ISO 5752 SERIES 192 |  | ISO 5752 SERIES 3 | ISO 5752 SERIES 4 | ISO 5752 SERIES 7 | ISO 5752 SERIES 14 | ISO 5752 SERIES 15 | ISO 5752 SERIES 18 | ISO 5752 SERIES 19 | ISO 5752 SERIES 26 | [5 empty] | ISO 5752 | ISO 5752 | ISO 5752 | ISO 5752 | ISO 5752 | ISO 5752 | ISO 5752 | ISO 5752 SERIES 4 | ISO 5752 SERIES 19 | ISO 5752 SERIES 14 | ISO 5752 SERIES 15 | ISO 5752 SERIES 26 |  | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 19 | ISO 5752 SERIES 4 |  |  | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 18 | ISO 5752 SERIES 7 | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 3 | ISO 5752 SERIES 4 | ISO 5752 SERIES 15 | ISO 5752 SERIES 26 | ISO 5752 SERIES 19 | ISO 5752 SERIES 19 | ISO 5752 SERIES 18 | ISO 5752 SERIES 7 | ISO 5752 SERIES 19 | ISO 5752 SERIES 4 | ISO 5752 SERIES 19 | ISO 5752 SERIES 4 | ISO 5752 SERIES 14 |  | ISO 5752 SERIES 18 |  |  | ISO 5752 SERIES 3 | ISO 5752 SERIES 15 | ISO 5752 SERIES 7 |  | ISO 5752 SERIES 4 | ISO 5752 SERIES 19 | [7 empty] | ISO 5752 SERIES 15 | ISO 5752 SERIES 3 | ISO 5752 SERIES 15 | ISO 5752 SERIES 4 | ISO 5752 SERIES 15 | ISO 5752 SERIES 4 SERIES 19
DIN EN 558 (DIN 3202-1) | [13 empty] | DIN 3202-1 SERIES F4 | DIN 3202-1 SERIES F5 |  |  | DIN 3202-1 SERIES F7 |  |  |  | DIN 3202-1 SERIES F19 |  |  | DIN 3202-1 SERIES F4 | DIN 3202-1 SERIES F5 | DIN 3202-1 SERIES F7 | [5 empty] | DIN 3202-1 | DIN 3202-1 | DIN 3202-1 | DIN 3202-1 | [6 empty] | DIN 3202-1 SERIES F4 | [9 empty] | DIN 3202-1 SERIES F5 | DIN 3202-1 SERIES F7 | [8 empty] | DIN 3202-1 SERIES F4 | [5 empty] | DIN 3202-1 SERIES F5 | [11 empty] | DIN 3202-1 SERIES F5 |  | DIN 3202-1 SERIES F5 |  | DIN 3202-1 SERIES F5
ASME B16.10 |  |  |  |  | ASME B16.10 CLASS 125 FF CLASS 300 RF |  |  | ASME B16.10 CLASS 125 FF CLASS 300 RF |  |  | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 300 |  |  |  |  | ASME 16.10 CLASS 250 | [6 empty] | ASME B16.10 CLASS 125 FF CLASS 300 RF |  |  |  | ASME B16.10 CLASS 250 | ASME B16.10 CLASS 300 | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 300 | ASME 16.10 CLASS 250 |  |  |  |  | ASME B16.10 | ASME B16.10 | ASME B16.10 | ASME B16.10 | ASME B16.10 |  |  | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 125 FF CLASS 300 RF |  |  | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 125 FF CLASS 300 RF | ASME B16.10 CLASS 300 |  |  | ASME B16.10 CLASS 250 | ASME B16.10 CLASS 250 |  |  | ASME B16.10 CLASS 250 | ASME B16.10 CLASS 300 | ASME B16.10 CLASS 250 | ASME B16.10 CLASS 300 | [5 empty] | ASME B16.10 CLASS 125 FF CLASS 300 RF |  |  |  | ASME B16.10 CLASS 300 | ASME B16.10 CLASS 250 | [8 empty] | ASME B16.10 CLASS 125 FF CLASS 300 RF |  | ASME B16.10 CLASS 300 |  | ASME B16.10 CLASS 300
MSS SP-81 | [9 empty] | MSS SP-81 | [31 empty] | MSS SP-81
BS 2080:1989 |  |  | BS 2080 PN10 ~ PN40 SERIES 7 | BS 2080 PN25 ~ PN40 SERIES 18 | [7 empty] | BS 2080 SERIES 4 | BS 2080 SERIES 7 | BS 2080 PN6 SERIES 14 |  | BS 2080 PN25 ~ PN40 SERIES 18 | BS 2080 PN25 ~ PN40 SERIES 19 | [6 empty] | BS 2080 SERIES 3 | BS 2080 PN6 SERIES 14 |  |  | BS 2080 PN25 ~ PN40 SERIES 19 | BS 2080 SERIES 4 | BS 2080 SERIES 3 | BS 2080 SERIES 4 | BS 2080 PN25 ~ PN40 SERIES 19 | BS 2080 PN6 SERIES 14 |  |  |  | BS 2080 SERIES 3 | BS 2080 SERIES 3 | BS 2080 SERIES 3 | BS 2080 PN25 ~ PN40 SERIES 19 | BS 2080 SERIES 4 |  | BS 2080 BS EN 558 | BS 2080 BS EN 558 | BS 2080 BS EN 558 | BS 2080 BS EN 558 | BS 2080 | BS 2080 | BS 2080 | BS 2080 | BS 2080 | BS 2080 BS EN 558 |  |  | BS 2080 | BS 2080 BS EN 558 | BS 2080 | BS 2080 | BS 2080 BS EN 558 | BS 2080 | BS 2080 BS EN 558 | BS 2080 | BS 2080 PN6 SERIES 14 |  | BS 2080 PN25 ~ PN40 SERIES 18 |  |  | BS 2080 SERIES 3 |  | BS 2080 SERIES 7 |  | BS 2080 SERIES 4 | BS 2080 PN25 ~ PN40 SERIES 19 | [8 empty] | BS 2080 SERIES 3 |  | BS 2080 SERIES 4 |  | BS 2080 SERIES 4
JIS B 2002:1987 |  |  | JIS B 2002 SERIES 81 PN10 ~ PN50 | JIS B 2002 SERIES 31 PN10 ~ PN25 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | [5 empty] | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 81 PN10 ~ PN50 | JIS B 2002 SERIES 1 | JIS B 2002 SERIES 7 PN10 ~ PN25 | JIS B 2002 SERIES 31 PN10 ~ PN25 | JIS B 2002 SERIES 115 PN50 | [6 empty] | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 1 | JIS B 2002 SERIES 7 PN10 ~ PN25 |  | JIS B 2002 SERIES 115 PN50 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 115 PN50 | JIS B 2002 SERIES 1 | JIS B 2002 SERIES 7 PN10 ~ PN25 |  |  | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 11s PN50 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 |  | JIS B 2002 SERIES 1 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 31 PN10 ~ PN25 | JIS B 2002 SERIES 81 PN10 ~ PN50 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 7 PN10 ~ PN25 |  | JIS B 2002 SERIES 11s PN50 | JIS B 2002 SERIES 11s PN50 | JIS B 2002 SERIES 31 PN10 ~ PN25 | JIS B 2002 SERIES 81 PN10 ~ PN50 | JIS B 2002 SERIES 115 PN50 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 115 PN50 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 | JIS B 2002 SERIES 6 10K PN10 ~ PN20 | JIS B 2002 SERIES 7 PN10 ~ PN25 | JIS B 2002 SERIES 10 20K PN25 ~ PN50 | JIS B 2002 SERIES 7 PN10 ~ PN25 | JIS B 2002 SERIES 10 20K PN25 ~ PN50
GB/T 12221:2005 |  |  |  |  | GB/T 12221 |  |  | GB/T 12221 |  |  | GB/T 12221 | GB/T 12221 |  |  | GB/T 12221 |  | GB/T 12221 | [6 empty] | GB/T 12221 |  | GB/T 12221 |  | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 |  | GB/T 12221 |  |  | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 |  |  | GB/T 12221 | GB/T 12221 | GB/T 12221 |  |  | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 |  | GB/T 12221 | GB/T 12221 |  |  | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | [5 empty] | GB/T 12221 | GB/T 12221 |  |  | GB/T 12221 | [8 empty] | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221 | GB/T 12221
VALVE DESIGN PRODUCT SPECIFICATION |  | AS 1628 |  |  | AS/NZS 2638.1 |  |  | AS/NZS 2638.2 |  | AS 6401 | EN 117115 EN 198418 | EN 117116 EN 198418 | EN 12288 | EN 117114 | EN 117115,16 EN 198418 | EN 12288 | EN 117116 EN 198418 | EN 117116 EN 198418 | EN 117115 EN 198418 | EN 117115 EN 198418 | EN 117117 EN 198418 | EN 12288 | NOT USED | API 6D (ISO 14313)23 API 60019 API 602 ISO 15761 ISO 10434 ISO 6002 ISO 5996 ISO 7259 | ISO 6002 ISO 5996 | ISO 6002 ISO 5996 | ISO 6002 | ISO 5996 ISO 7259 | API 6D (ISO 14313) API 60019 API 602 ISO 15761 ISO 10434 ISO 6002 ISO 5996 | DIN EN 117115 DIN EN 198418 | DIN EN 1171 DIN EN 1984 | DIN EN 1171 DIN EN 1984 | DIN EN 1171 DIN EN 1984 DIN 3352 PART 2, 4 | DIN EN 1171 DIN EN 1984 DIN 3352 PART 6, 7, 9, 10 | DIN EN 1171 DIN EN 1984 DIN 3352 PART 6, 7, 9, 10 | DIN 3352 PART 11 | MSS-SP 7013 AWWA C500 AWWA C509 AWWA C515 | API 6D (ISO 14313)23 API 60019 API 602 API 60320 ISO 15761 ISO 10434 | API 6D (ISO 14313)23 AWWA C500 AWWA C509 AWWA C515 ISO 15761 ISO 10434 | MSS-SP 70 AWWA C500 AWWA C509 AWWA C515 | API 6D (ISO 14313) API 60019 API 602 API 60320 AWWA C500 AWWA C509 AWWA C515 ISO 15761 ISO 10434 | MSS SP-81 AWWA C520 | BS 515012 PN6~PN1011 BS EN 1171 | BS 1414 BS EN 1984 | BS 5163 BS 5150 PN10~PN16 BS EN 1171 | BS 5163 BS EN 1171 | BS 5154 BS EN 12288 | BS 5154 BS EN 12288 | BS EN 1984 | BS 516312 PN10~PN16 BS EN 1171 | BS 5352 BS EN 1984 | BS 1414 BS EN 1984 | BS EN 117115,16 BS EN 198418 | EN 117116 EN 198418 | BS 5163 BS 515012 PN25 BS EN 1171 | BS 5163 BS EN 1171 | BS 5154 BS EN 12288 | BS 5154 BS EN 12288 | BS EN 1984 | BS EN 1984 | BS 5163 PN25 BS EN 1171 | BS 5352 BS EN 1984 | JIS B 2031 | JIS B 2031 | JIS B 2011 | JIS B 2011 | JIS B 2031 | JIS B 2031 | JIS B 2031 | JIS B 2011 | JIS B 2031 | JIS B 2031 | JIS B 2031 | JIS F 7367 | JIS F 7363 JIS F 7360 | JIS F 7368 | JIS F 7364 | JIS F 7366 | JIS F 7369 | JIS B 2031 | JIS B 2031 | GB/T 12232 JB/T 5298 | GB/T 12232 JB/T 5298 | GB/T 12232 JB/T 5298 | GB/T 12232 JB/T 5298 | GB/T 12232 JB/T 5298
DN | NPS | SHORT | ISO 5752 SERIES |  | DUCTILE CAST IRON |  |  | DUCTILE CAST IRON |  | DUCTILE CAST IRON STAINLESS STEEL | EN 558 SERIES 3 | EN 558 SERIES 4 | COPPER ALLOY VALVES | GREY CAST IRON VALVES | EN 558 SERIES 15 | COPPER ALLOY VALVES | EN 558 SERIES 19 | EN 558 SERIES 26 | EN 558 SERIES 29 | EN 558 SERIES 30 | EN 558 SERIES 45 | COPPER ALLOY VALVES | FLANGED AND WAFER TYPES | ISO 5752 SERIES 3 | ISO 5752 SERIES 14 | ISO 5752 SERIES 15 | ISO 5752 SERIES 26 | ISO 5752 SERIES 19 | ISO 5752 SERIES 4 | EN 558 SERIES 3 | EN 558 SERIES 4 | EN 558 SERIES 19 | DIN 3202 SERIES F4 | DIN 3202 SERIES F5 | DIN 3202 SERIES F7 | DIN 3202 SERIES F9 | FLAT FACE | RAISED FACE |  | RAISED FACE | RAISED FACE | RAISED FACE | CAST IRON | WEDGE GATE PETROLEUM | CAST IRON | PARALLEL SLIDE | COPPER ALLOY |  | PARALLEL SLIDE | WATERWORKS | WADGE GATE PETROLEUM ≤ 2" | WEDGE GATE PETROLEUM | BS EN 558 SERIES 15 | BS EN 558 SERIES 26 | CAST IRON | PARALLEL SLIDE | COPPER ALLOY |  | PARALLEL SLIDE |  | WATERWORKS | WADGE GATE PETROLEUM ≤ 2" | FOR GENERAL MECHANICAL EQUIPMENT | [10 empty] | FOR SHIP | [5 empty] | FOR OUTDOOR WATERWORKS10 |  | SHORT | LONG | GB/T 12221 SERIES 4 | GB/T 12221 SERIES 15 | GB/T 12221 SERIES 4/19
|  |  | PREFFERED FOR CLASS 35 (PN40) | PREFFERED FOR CLASS 14 AND 21 (PN16 AND PN 20) | [28 empty] | EN 558 SERIES 14 | EN 558 SERIES 15 | EN 558 SERIES 26 | EN 558:2017 SERIES 47 | CAST IRON | STEEL |  | CAST IRON | STEEL | STAINLESS STEEL OR STAINLESS-STEEL LINED |  | STEEL |  | CAST IRON |  |  | STEEL | CAST IRON | STEEL | STEEL |  |  |  | CAST IRON |  |  | STEEL |  | CAST IRON | STEEL | ALL MATERIALS | CAST IRONS | BRONZE, STAINLESS STEEL | BRONZE, STAINLESS STEEL | CAST IRONS | ALL MATERIALS | ALL MATERIALS | BRONZE, STAINLESS STEEL | CAST IRONS | ALL MATERIALS | CAST IRONS | BRONZE, STAINLESS STEEL | CAST IRONS | BRONZE, STAINLESS STEEL | CAST IRONS | STEELS | CAST IRONS | ALL MATERIALS
[5 empty] | WITHOUT BY-PASS |  | WITH INTEGRAL BY-PASS | WITOUT BY-PASS | WITH INTEGRAL BY-PASS | FLANGED, WAFER OR LUGGED |  |  | EN 558 SERIES 77 | EN 558 SERIES 143 |  | EN 558 SERIES 187 | [5 empty] | EN 558 SERIES 477 | EN 558 SERIES 94 | [13 empty] | SOLID WEDGE AND DOUBLE DISC | SOLID WEDGE AND DOUBLE DISC | CONDUIT | SOLID WEDGE AND DOUBLE DISC | SOLID WEDGE, DOUBLE DISC AND CONDUIT | 0°C TO 66°C | BS EN 558 SERIES 14 | BS EN 558 SERIES 3 | BS EN 558 SERIES 3 | BS EN 558 SERIES 3 | BS 2080 SERIES 18 | BS 2080 SERIES 7 | BS 2080 SERIES 3 | BS 2080 SERIES 3 | BS 2080 SERIES 3 | BS EN 558 SERIES 4 |  |  | BS 2080 SERIES 19 | BS EN 558 SERIES 19 CLASS 250 | BS 2080 SERIES 18 | BS 2080 SERIES 7 | BS EN 558 SERIES 19 CLASS 250 | BS 2080 SERIES 4 | BS EN 558 SERIES 19 CLASS 250 | BS 2080 SERIES 4 | JIS B 2002 SERIES 1 | JIS B 2002 SERIES 2 | JIS B 2002 SERIES 3 | JIS B 2002 SERIES 4 | JIS B 2002 SERIES 5 | JIS B 2002 SERIES 6 | JIS B 2002 SERIES 7 | JIS B 2002 SERIES 8 | JIS B 2002 SERIES 9 | JIS B 2002 SERIES 10 | JIS B 2002 SERIES 11 | JIS B 2002 SERIES 101 | JIS B 2002 SERIES 102 | JIS B 2002 SEREIS 103 | JIS B 2002 SERIES 104 | JIS B 2002 SERIES 105 | JIS B 2002 SERIES 106 | JIS B 2002 SERIES 201 | JIS B 2002 SERIES 7 | GB/T 12221 SERIES 3 | GB/T 12221 SERIES 15
|  | PN16, PN20, PN40 CLASS 14, 21, 35 | AS 1628 SERIES 7 | AS 1628 SERIES 18 | AS/NZS 2638.1 PN16 | AS/NZS 2638.1 PN35 | AS/NZS 2638.1 PN16, PN35 | AS/NZS 2638.2 PN16, PN25 |  | AS 6401 PN6, PN10, PN1621 | PN6 ~ PN1622 CLASS 125 ~ 150 | PN25 ~ PN40 CLASS 250 ~ 300 | PN6 ~ PN40 CLASS 125 ~ 300 | PN6 ~ PN16 | PN6 ~ PN40 | PN6 ~ PN40 CLASS 125 ~ 300 | PN25 ~ PN40 CLASS 250 ~ 300 | PN25 ~ PN100 | PN6 ~ PN16 | PN6 ~ PN16 | PN25 ~ PN40 | PN6 ~ PN40 | PN6 ~ PN40 | PN6 ~ PN16 CLASS 125 ~ 150 | PN6 ~ PN16 |  | PN25 ~ PN40 | CLASS 250 | CLASS 300 | PN6 ~ PN16 CLASS 125 ~ 150 | CLASS 300 | CLASS 250 | PN6 ~ PN 16 | PN6 ~ PN16, PN25, PN40 | PN25, PN40, PN63, PN100 | PN6 ~ PN40 | ASME B16.10 CLASS 1258 | ASME B16.10 CLASS 150 |  | ASME B16.10 CLASS 250 | ASME B16.10 CLASS 3009 | MSS SP-81 MINIMUM DESIGN PRESSUR RATING 10.3 BAR | PN6 ~ PN16 | PN10 ~ PN16 CLASS 125 ~ 150 | [7 empty] | CLASS 300 | PN6 ~ PN40 | PN25 ~ PN100 | PN25 ~ PN40 CLASS 250 ~ 300 | [7 empty] | ISOMORPHIC | 5K | PN10 ~ PN25 | 10K | 10K | PN10 ~ PN20 10K | PN10 ~ PN25 | PN10 ~ PN50 | 16K | PN25 ~ PN50 20K | PN50 | 5K | 5K | 10K | 10K | 10K | 16K | 4.5K, 7.5K, 10K | 16K, 20K | PN10 ~ PN25 |  | PN25 ~ PN50 | PN25 | PN40
8 | 0.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
10 | 0.375 | 70 | 108 | 80 | - | - | - | - | - | - | 102 | - | 108 | 115 | - | 80 | - | - | 108 | - | - | - | - | 102 | 115 | - | - | - | - | 102 | - | - | 110 | - | - | - | - | 102 | - | - | - | - | 115 | - | 102 | - | 80 | 108 | - | - | - | - | - | - | - | - | 80 | 108 | - | - | - | - | - | - | 80 | - | - | 102 | - | 108 | - | - | - | - | - | - | - | - | - | - | - | 102 | - | - | - | -
15 | 0.5 | 70 | 108 | 80 | - | - | - | - | - | - | 108 | 140 | 108 | 115 | - | 80 | 140 | - | 108 | 150 | 140 | - | - | 108 | 115 | - | - | - | 140 | 108 | 140 | 140 | 115 | - | - | - | - | 108 | - | - | 140 | - | 115 | - | 108 | - | 80 | 108 | - | - | 108 | 140 | - | - | 140 | - | 80 | 108 | - | - | - | 140 | - | - | 80 | - | - | 108 | - | 108 | - | 140 | 140 | 90 | - | 100 | - | - | - | - | - | 108 | - | 140 | - | 140
20 | 0.75 | 73 | 117 | 90 | - | - | - | - | - | - | 117 | 152 | 117 | 120 | - | 90 | 152 | - | 117.5 | 160 | 152 | 75 | - | 117 | 120 | - | - | - | 152 | 117 | 152 | 152 | 120 | - | - | 75 | - | 117 | - | - | 152 | - | 120 | - | 117 | - | 90 | 117 | - | - | 117 | 152 | - | - | 152 | - | 90 | 117 | - | - | - | 152 | - | - | 90 | - | - | 117 | - | 117 | - | 152 | 152 | 100 | - | 110 | - | - | - | - | - | 117 | - | 152 | - | 152
25 | 1 | 89 | 127 | 100 | - | - | - | - | - | - | 127 | 165 | 127 | 125 | 120 | 100 | 165 | - | 127 | 160 | 210 | 80 | 25 | 127 | 125 | 120 | - | - | 165 | 127 | 165 | 165 | 125 | 120 | - | 80 | - | 127 | - | - | 165 | - | 125 | 127 | 127 | - | 100 | 127 | - | - | 127 | 165 | 120 | - | 165 | - | 100 | 127 | - | - | - | 165 | - | - | 100 | 100 | - | 127 | - | 127 | - | 165 | 165 | 110 | - | 120 | - | - | - | - | - | 127 | - | 165 | - | 165
32 | 1.25 | 102 | 146 | 110 | - | - | - | - | - | - | 140 | 178 | 146 | 130 | 140 | 110 | 178 | - | 127 | 180 | 230 | 90 | 32 | 140 | 130 | 140 | - | - | 178 | 140 | 178 | 178 | 130 | 140 | - | 90 | - | 140 | - | - | 178 | - | 130 | 140 | 140 | - | 110 | 146 | - | - | 140 | 178 | 140 | - | 178 | - | 110 | 146 | - | - | - | 178 | - | - | 110 | 110 | - | 140 | - | 146 | - | 178 | 178 | 130 | - | 140 | - | - | - | - | - | 140 | - | 178 | - | 178
40 | 1.5 | 118 | 159 | 120 | - | - | - | - | - | - | 165 | 190 | 159 | 140 | 240 | 120 | 190 | 240 | 136 | 190 | 240 | 100 | 40 | 165 | 140 | 240 | 240 | - | 190 | 165 | 190 | 190 | 140 | 240 | 240 | 100 | - | 165 | - | - | 190 | - | 140 | 165 | 165 | 165 | 120 | 159 | 165 | - | 165 | 190 | 240 | 240 | 190 | 190 | 120 | 159 | 190 | 190 | - | 190 | 140 | - | 120 | 125 | 165 | 165 | 240 | 159 | - | 190 | 190 | 140 | - | 150 | - | - | - | - | - | 165 | 240 | 190 | 240 | 190
50 | 2 | 143 | 190 | 135 | - | - | - | - | - | 48 | 178 | 216 | 190 | 150 | 250 | 135 | 216 | 250 | 142 | 200 | 250 | 110 | 50 | 178 | 150 | 250 | 250 | 216 | 216 | 178 | 216 | 216 | 150 | 250 | 250 | 110 | 178 | 178 | 178 | 216 | 216 | 48 | 150 | 178 | 178 | 178 | 135 | 190 | 178 | 178 | 178 | 216 | 250 | 250 | 216 | 216 | 135 | 190 | 216 | 216 | 216 | 216 | 150 | 160 | 135 | 140 | 180 | 178 | 250 | 190 | 200 | 216 | 216 | - | 180 | - | 200 | 200 | 210 | 180 | 250 | 178 | 250 | 216 | 250 | 216
65 | 2.5 | 156 | 216 | 165 | - | - | - | - | - | 48 | 190 | 241 | 216 | 170 | 270 | 165 | 241 | 290 | 154 | 215 | 270 | 130 | 65 | 190 | 170 | 270 | 290 | 241 | 241 | 190 | 241 | 241 | 170 | 270 | 290 | 150 | 190 | 190 | 190 | 241 | 241 | - | 170 | 190 | 190 | 190 | 165 | 216 | 190 | 190 | - | 241 | 270 | 290 | 241 | 241 | 165 | 216 | 241 | 241 | 241 | - | 170 | 170 | 165 | 170 | 190 | 190 | 270 | 216 | 220 | 241 | 241 | - | 190 | - | 220 | 220 | 240 | - | - | 190 | 270 | 241 | 270 | 241
80 | 3 | 172 | 254 | 185 | 203 | 280 | - | 203 | - | 51 | 203 | 283 | 254 | 180 | 280 | 185 | 283 | 310 | 160 | 230 | 280 | 150 | 80 | 203 | 180 | 280 | 310 | 283 | 283 | 203 | 283 | 283 | 180 | 280 | 310 | 150 | 203 | 203 | 203 | 282 | 282 | 51 | 180 | 203 | 203 | 203 | 185 | 254 | 203 | 203 | - | 283 | 280 | 310 | 283 | 283 | 185 | 254 | 283 | 283 | 283 | - | 180 | 180 | 185 | 190 | 200 | 203 | 280 | - | 230 | 283 | 283 | - | 200 | - | 230 | 230 | 260 | 240 | 280 | 203 | 280 | 283 | 280 | 283
90 | 3.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 190 | - | - | 210 | 216 | - | - | 240 | 300 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
100 | 4 | 210 | 305 | - | 229 | 305 | - | 229 | - | 51 | 229 | 305 | 305 | 190 | 300 | 229 | 305 | 350 | 172 | 250 | 300 | 160 | 100 | 229 | 190 | 300 | 350 | 305 | 305 | 229 | 305 | 305 | 190 | 300 | 350 | 160 | 229 | 229 | 229 | 305 | 305 | 51 | 190 | 229 | 229 | 229 | 229 | 305 | 229 | 229 | - | 305 | 300 | 350 | 305 | 305 | 229 | 305 | 305 | 305 | 305 | - | 190 | 200 | - | - | 230 | 229 | 300 | - | 250 | 305 | 305 |  | 230 | - | 250 | 250 | 290 | 250 | 300 | 229 | 300 | 305 | 300 | 305
125 | 5 | - | - | - | - | - | - | - | - | 57 | 254 | 381 | 356 | 200 | 325 | - | 381 | 400 | 186 | 275 | 350 | 200 | 125 | 254 | 200 | 325 | 400 | 381 | 381 | 254 | 381 | 381 | 200 | 325 | 400 | 200 | 254 | 254 | - | 381 | 381 | 57 | 200 | - | 254 | 254 | - | - | 254 | 254 | - | - | 325 | 400 | 381 | 381 | - | - | 381 | 381 | 381 | - | 200 | 220 | - | - | 250 | 254 | 325 | - | 270 | 381 | 381 | - | 250 | - | 270 | 270 | 310 | 260 | 325 | 254 | 325 | 381 | 325 | 381
150 | 6 | - | - | - | 267 | 330 | - | 267 | - | 57 | 267 | 403 | 406 | 210 | 350 | - | 403 | 450 | 200 | 300 | 375 | 210 | 150 | 267 | 210 | 350 | 450 | 403 | 403 | 267 | 403 | 403 | 210 | 350 | 450 | 210 | 267 | 267 | 267 | 403 | 403 | 57 | 210 | 267 | 267 | 267 | - | - | 267 | 267 | - | 403 | 350 | 450 | 403 | 403 | - | - | 403 | 403 | 403 | - | 210 | 240 | - | - | 270 | 267 | 350 | - | 290 | 403 | 403 | - | 270 | - | 290 | 290 | 330 | 280 | 350 | 267 | 350 | 403 | 350 | 403
200 | 8 | - | - | - | 292 | 380 | - | 292 | - | 70 | 292 | 419 | 521 | 230 | 400 | - | 419 | 550 | 228 | 350 | 425 | - | 200 | 292 | 230 | 400 | 550 | 419 | 419 | 292 | 419 | 419 | 230 | 400 | 550 | - | 292 | 292 | 292 | 419 | 419 | 70 | 230 | 292 | 292 | 292 | - | - | 292 | 292 | - | 419 | 400 | 550 | 419 | 419 | - | - | 419 | 419 | 419 | - | 230 | 260 | - | - | 290 | 292 | 400 | - | 320 | 419 | 419 | - | 290 | - | 320 | 310 | 370 | 300 | 400 | 292 | 400 | 419 | 400 | 419
225 | 9 | - | - | - | 305 | 405 | - | 305 | - | 70 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
250 | 10 | - | - | - | 330 | 420 | - | 330 | - | 70 | 330 | 457 | 635 | 250 | 450 | - | 457 | 650 | 255 | 400 | 450 | - | - | 330 | 250 | 450 | 650 | 457 | 457 | 330 | 457 | 457 | 250 | 450 | 650 | - | 330 | 330 | 330 | 457 | 457 | 70 | 250 | 330 | 330 | 330 | - | - | 330 | 330 | - | 457 | 450 | 650 | 457 | 457 | - | - | 457 | 457 | 457 | - | 250 | 300 | - | - | 330 | 330 | 450 | - | 380 | 457 | 457 | - | 330 | - | 380 | 340 | 430 | 380 | 450 | 330 | 450 | 457 | 450 | 457
300 | 12 | - | - | - | 356 | 430 | - | 356 | - | 76 | 356 | 502 | 749 | 270 | 500 | - | 502 | 750 | 285 | 425 | 500 | - | - | 356 | 270 | 500 | 750 | 502 | 502 | 356 | 502 | 502 | 270 | 500 | 750 | - | 356 | 356 | 356 | 502 | 502 | 76 | 270 | 356 | 356 | 356 | - | - | 356 | 356 | - | 502 | 500 | 750 | 502 | 502 | - | - | 502 | 502 | 502 | - | 270 | - | - | - | 350 | 356 | 500 | - | 440 | 502 | 502 | - | 370 | - | 440 | 380 | 490 | 400 | 500 | 356 | 500 | 502 | 500 | 502
350 | 14 | - | - | - | 381 | 550 | - | 381 | - | 76 | 381 | 762 | - | 290 | 550 | - | 572 | 850 | 315 | 475 | 550 | - | - | 381 | 290 | 550 | 850 | 572 | 762 | 381 | 762 | 572 | 290 | 550 | 850 | - | 381 | 381 | 381 | 572 | 762 | 76 | 290 | 381 | 381 | 381 | - | - | 381 | 381 | - | 762 | 550 | 850 | 572 | 572 | - | - | 572 | 762 | 572 | - | 290 | - | - | - | 381 | 381 | 550 | - | - | 762 | 572 | - | 410 | - | 500 | 420 | 540 | 430 | 550 | 381 | 550 | 762 | 550 | 572
375 | 15 | - |  |  | 381 | 610 | - | 381 | - | 89 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
400 | 16 | - | - | - | 406 | 600 | - | 406 | - | 89 | 406 | 838 | - | 310 | 600 | - | 610 | 950 | 340 | 525 | 600 | - | - | 406 | 310 | 600 | 950 | 610 | 838 | 406 | 838 | 610 | 310 | 600 | 950 | - | 406 | 406 | 406 | 610 | 838 | 89 | 310 | 406 | 406 | 406 | - | - | 406 | 406 | - | 838 | 600 | 950 | 610 | 610 | - | - | 610 | 838 | 610 | - | 310 | - | - | - | 406 | 406 | 600 | - | - | 838 | 610 | - | 470 | - | 590 | 480 | 610 | 470 | 600 | 406 | 600 | 838 | 600 | 610
450 | 18 | - | - | - | 432 | 660 | 660 | 432 | 660 | 89 | 432 | 914 | - | 330 | 650 | - | 660 | 1050 | 360 | 575 | - | - | - | 432 | 330 | 650 | 1050 | 660 | 914 | 432 | 914 | 660 | 330 | 650 | - | - | 432 | 432 | 432 | 660 | 914 | 89 | 330 | 432 | 432 | 432 | - | - | 432 | 432 | - | 914 | 650 | 1050 | 660 | 660 | - | - | 660 | 914 | 660 | - | 330 | - | - | - | 432 | 432 | 650 | - | - | 914 | 660 | - | 500 | - | 640 | - | - | 500 | 650 | 432 | 650 | 914 | 650 | 660
500 | 20 | - | - | - | 457 | 710 | 710 | 457 | 710 | 114 | 457 | 991 | - | 350 | 700 | - | 711 | 1150 | 380 | 625 | - | - | - | 457 | 350 | 700 | 1150 | 711 | 991 | 457 | 991 | 711 | 350 | 700 | 1150 | - | 457 | 457 | 457 | 711 | 991 | 114 | 350 | 457 | 457 | 457 | - | - | 457 | 457 | - | 991 | 700 | 1150 | 711 | 711 | - | - | 711 | 991 | 711 | - | 350 | - | - | - | 457 | 457 | 700 | - | - | 991 | 711 | - | 550 | - | 710 | - | - | 530 | 700 | 457 | 700 | 991 | 700 | 711
550 | 22 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 508 | - | 1092 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 483 | 750 | - | - | 1092 | 749 | - | 600 | - | 780 | - | - | - | - | - | - | - | - | -
600 | 24 | - | - | - | 508 | 785 | 785 | 508 | 785 | 114 | 508 | 1143 | - | 390 | 800 | - | 787 | 1350 | 425 | 725 | - | - | - | 508 | - | 800 | 1350 | 787 | 1143 | 508 | 1143 | 787 | 390 | 800 | 1350 | - | 508 | 508 | 508 | 787 | 1143 | 114 | 390 | 508 | 508 | 508 | - | - | 508 | 508 | - | 1143 | 800 | 1350 | 787 | 787 | - | - | 787 | 1143 | 787 | - | 390 | - | - | - | 508 | 508 | 800 | - | - | 1143 | 787 | - | 660 | - | 850 | - | - | 560 | 800 | 508 | 800 | 1143 | 800 | 787
RED ITALIC LETTERS INDICATE HISTORICAL ORIGIN | [6 empty] | © COPYRIGHT PROTECTED. IT IS ILLIEGAL TO COPY OR REPRODUCE THIS DOCUMENT HOWEVER, IT IS PERMISSIBLE TO LINK TO THIS WEBSITE SUBMISSION. | [75 empty] | RED ITALIC LETTERS INDICATE HISTORICAL ORIGIN
1. | APPLIES TO BRONZE AND FURTHER MAY APPLY TO STAINLESS STEEEL FOR BUILDING EQUIPMENT
2. | EXISTING SIZES FROM THIS SERIES CAN BE CONSIDERED SAME AS SERIES 19 WITHIN DESIGNATED ACCURACY
3. | THIS SERIES IS USED FOR GREY CAST IRON GATE VALVES ISOMORPHIC SERIES (DETAILS SEE RELEVANT PRODUCT STANDARDS)
4. | UP TO DN80 - GATE, GLOBE AND CHECK VALVES - ALL PN RATINGS
5. | APPLIES TO CAST IRONS (GREY CAST IRON, NODULAR GRAPHITE CAST IRON, AND BLACK HEART MEALLEABLE CAST IRON).
6. | UP TO DN100 - GATE, GLOBE AND CHECK VALVES - ALL PN RATINGS
7. | THIS SERIES APPLIES TO COPPER ALLOY VALVES ONLY; NOT TO BE USED FOR CAST IRON OR STEEL VALVES
8. | FOR DN350 AND ABOVE SOLID WEDGE ONLY
9. | FOR DN15 TO DN32 SOLID WEDGE ONLY
10. | IN THIS CONTEXT, NOMINAL DIAMETER 80 IS REPLACED BY NOMINAL DIAMETER 75
11. | FOR PN10 UP TO DN150
12. | DIFFERENT ACCURACIES THAN STATED
13. | DOUBLE DISK (PARALLEL SEAT) UP TO DN450
14. | ISOMORFIC TO DN40 TO DN1000; PN6~PN16 DN40 TO DN500
15. | DN40 TO DN1000
16. | PN25 ONLY, DN40 TO DN600
17. | PN25 ONLY, DN40 TO DN400
18. | ONLY FOR PN10, PN16, PN25, PN40, PN63, PN100, CLASS 150, 300, AND 600
19. | STARTING FROM DN25. ANSI CLASS ONLY
20. | STARTING FROM DN15
21. | PN16 ONLY UP TO DN450
22. | NON-PREFERRED
23. | STARTS FROM DN50; DOES NOT INCLUDE DN125; CLASS 150 ONLY
~ World's Largest Valve & Actuation Stock Range ~
Global Supply Line provides this technical information to assist the valve community. Please share and refer us to any specifiers or purchasers of valves/actuators within your network.
Click here for our full online stock list https://www.globalsupplyline.com.au/stock-list-valves/
© Copyright Global Supply Line 2024